## Slide 1: Pre-blended supply labelling
Ventilator 8mm PU tube
Clinician selects the prescribed FiO2 concentration
Quick release connectors makes it easy to switch
Cut or printed plate
Cable ties
(single row of 3 might suffice)
Compressed air hoses
(2, 3 or 4 off)
This forms part of the ward infrastructure and not the ventilator itself

## Slide 2: Proposed components
There is no standard connector key for pre-blended gas.
Therefore, use a standard universal connector – which is readily available at the national level.
The risk of incorrect connections is mitigated by labelling.
If using an industrial connector, then flush clean with warn detergent water and rinse with clean water before use.
Conventional gas lines may be costly. Consider using standard pneumatic 16mm PU hoses or 15mm copper pipes.
8mm x 2m PU tube to ventilator
Gas supply line
Ventilator
Supply

## Slide 3: Standard medical gas systems
Hoses are colour coded
Collar forms a key that prevents wrong connections
Hose is pushed over barbs and clamped
Beware of incompatibility between British, German, Scandinavian, US and Japanese standards
NOT REQUIRED